## Legend
Key for Reading Spreadsheets
At the top of each spreadsheet, the water requirements for each step in the generation process are listed. At the bottom of each spreadsheet, different technological options are combined and total estimates of water requirements are provided.
Water inputs for all energy sources (EXCEPT coal) are color coded as follows:
Agriculture
Mining
Transportation
Processing
Cooling
Cleaning
Evaporative Losses (hydroelectric facilities only)
Other
References and sources are identified with their numbers using the following code:
W= | Withdrawal
C= | Consumption
H= | High figure
L= | Low figure

## Bioenergy
Water Requirements for Bioenergy Power Production
All Numbers in m3/MWh
| BIOENERGY | Withdrawal |  | Consumption
|  | m^3/MWh |  | m^3/MWh
| Item | Low | High | Low | High | Notes/Assumptions | Sources
| Agriculture, Rapeseed | 359.9712 | 630 | 359.9712 | 630 | Data is originally all in terms of "water use efficiency". We use the same numbers for rates of withdrawal and consumption, assuming that all applied water (for irrigation) is evapo-transpired. Original study assumes that, for the lower numbers (more efficient systems) waste byproducts and harvest residues are used to generate electricity. | Berndes, 2002 [W,C/H,L]
| Agriculture, Sugarcane | 133 | 558 | 133 | 558 |  | Berndes, 2002 [W,C/H,L]
| Agriculture, Sugar Beet | 256 | 677 | 256 | 677 |  | Berndes, 2002 [W,C/H,L]
| Agriculture, Corn | 263 | 1250 | 263 | 1250 |  | Berndes, 2002 [W,C/H,L]
| Agriculture, Wheat | 144 | 1260 | 144 | 1260 |  | Berndes, 2002 [W,C/H,L]
| Biomass-based steam plant | 2.5198 | 2.5198 | 2.5198 | 2.5198 | Assumes a 23% specified efficiency and a HHV at 20 Gj/Mg | USDOE/EPRI, 1997 and Berndes, 2001 [W,C/H,L]
| Improved biomass-based steam plant | 1.7999 | 1.7999 | 1.7999 | 1.7999 | Assumes a 34% specified efficiency and a HHV of 20 GJ/Mg | USDOE/EPRI, 1997 and Berndes, 2001 [W,C/H,L]
| Gasification-based, combined cycle generation | 0.35997 | 0.35997 | 0.35997 | 0.35997 | Includes boiler feed water requirements but NOT wet scrubbing. Steam from the steam cycle is injected into the gasifier Asumes a specified efficiency of 36% and a HHV of 20 GJ/Mg. | USDOE/EPRI, 1997 and Berndes, 2002 [W,C/H,L]
| Quench feed water for wet scrubbing of syngas (exiting gasifier) | 0.10799 | 3.24 |  |  | For methanol. Hydrogen values are much higher. | Katofsky, 1993 and Berndes, 2002 [W,C/H,L]
| BIOGAS | Withdrawal |  | Consumption
|  | m^3/MWh |  | m^3/MWh
| Item | Low | High | Low | High | Notes/Assumptions | Sources
| Simple Cycle | 0.083649 | 0.083649 | 0.083649 | 0.083649 | Assumes a 500 MW plant. Analysis assumes that water requirements for landfill gas facilities are comparable to those for conventional natural gas facilities. All data are taken from conventional natural gas facilities. | Maulbetsch 2006, EPRI, CATF et al. 2003
| Combined cycle, wet cooling | 0.87055 | 0.87055 | 0.6813 | 0.6813
| Combined cycle, dry cooling | 0.1514 | 0.1514 | 0 | 0
| Combined cycle, once-thru cooling | 9.084 | 75.7002 | 0.3785 | 0.3785
| Steam turbine, once-thru cooling | 75.7002 | 189.2506 | 1.1355 | 1.1355
| Steam turbine, wet cooling | 1.1355 | 3.028 | 0.9084 | 2.4224
| Steam turbine, dry cooling | 0.1514 | 0.1514 | 0 | 0
| Steam turbine, pond cooling | 1.1355 | 2.271 | 1.1355 | 1.8168
| Mining, combined cycle conversion technology | 0 | 0 | 0 | 0 | Unlike traditional natural gas, we assume no processing water needs (because landfill gas facilities often produce additional water by drying the captured gas). The processing water needed to produce energy from conventional natural gas is used in the pumping process.
| Transportation, combined cycle conversion technology | 0 | 0 | 0 | 0 | We assume no transportation costs, as energy is typically produced on-site (with landfill gas generation).
| Other | 0 | 0 | 0 | 0
| Inlet fogging (additional option) | 0.47313 | 0.6056 | 0.47313 | 0.6056 |  | Maulbetsch 2006
Bioenergy Power Production Method | [5 empty] | Withdrawal Water Requirement (m3/MWh) |  | Consumptive Water Requirement (m3/MWh)
Dedicated Energy Crops | [5 empty] | Low | High | Low | High
1 | Dedicated energy crops - rapeseed - gasification - |  |  |  |  | 360.3312 | 630.36 | 360.3312 | 630.36
2 | Dedicated energy crops - sugarcane - gasification - |  |  |  |  | 133.36 | 558.36 | 133.36 | 558.36
3 | Dedicated energy crops - Sugar beet - gasification - |  |  |  |  | 256.36 | 677.36 | 256.36 | 677.36
4 | Dedicated energy crops - Corn - gasification - |  |  |  |  | 263.36 | 1250.36 | 263.36 | 1250.36
5 | Dedicated energy crops - Wheat - gasification - |  |  |  |  | 144.36 | 1260.36 | 144.36 | 1260.36
6 | Dedicated energy crops - rapeseed - gasification - syngas scrubbing |  |  |  |  | 360.4392 | 633.6 | 360.3312 | 630.36
7 | Dedicated energy crops - sugarcane - gasification - syngas scrubbing |  |  |  |  | 133.468 | 561.6 | 133.36 | 558.36
8 | Dedicated energy crops - Sugar beet - gasification - syngas scrubbing |  |  |  |  | 256.468 | 680.6 | 256.36 | 677.36
9 | Dedicated energy crops - Corn - gasification - syngas scrubbing |  |  |  |  | 263.468 | 1253.6 | 263.36 | 1250.36
10 | Dedicated energy crops - Wheat - gasification - syngas scrubbing |  |  |  |  | 144.468 | 1263.6 | 144.36 | 1260.36
11 | Dedicated energy crops - rapeseed - Biomass-based steam plant - |  |  |  |  | 362.491 | 632.5198 | 362.491 | 632.5198
12 | Dedicated energy crops - sugarcane - Biomass-based steam plant - |  |  |  |  | 135.5198 | 560.5198 | 135.5198 | 560.5198
13 | Dedicated energy crops - Sugar beet - Biomass-based steam plant - |  |  |  |  | 258.5198 | 679.5198 | 258.5198 | 679.5198
14 | Dedicated energy crops - Corn - Biomass-based steam plant - |  |  |  |  | 265.5198 | 1252.5198 | 265.5198 | 1252.5198
15 | Dedicated energy crops - Wheat - Biomass-based steam plant - |  |  |  |  | 146.5198 | 1262.5198 | 146.5198 | 1262.5198
16 | Dedicated energy crops - rapeseed - Improved biomass-based steam plant - |  |  |  |  | 361.7711 | 631.7999 | 361.7711 | 631.7999
17 | Dedicated energy crops - sugarcane - Improved biomass-based steam plant - |  |  |  |  | 134.7999 | 559.7999 | 134.7999 | 559.7999
18 | Dedicated energy crops - Sugar beet - Improved biomass-based steam plant - |  |  |  |  | 257.7999 | 678.7999 | 257.7999 | 678.7999
19 | Dedicated energy crops - Corn - Improved biomass-based steam plant - |  |  |  |  | 264.7999 | 1251.7999 | 264.7999 | 1251.7999
20 | Dedicated energy crops - Wheat - Improved biomass-based steam plant - |  |  |  |  | 145.7999 | 1261.7999 | 145.7999 | 1261.7999
Waste Products
21 | Agricultural/Forestry Waste - gasification - |  |  |  |  | 0.35997 | 0.35997 | 0.35997 | 0.35997
22 | Agricultural/Forestry Waste - gasification - syngas scrubbing |  |  |  |  | 0.46796 | 3.6 | 0.35997 | 0.35997
23 | Agricultural/Forestry Waste - Biomass-based steam plant |  |  |  |  | 2.5198 | 2.5198 | 2.5198 | 2.5198
24 | Agricultural/Forestry Waste - Improved biomass-based steam plant |  |  |  |  | 1.7999 | 1.7999 | 1.7999 | 1.7999
Biogas (including landfill gas or WWTP gas - methane)
25 | Biogas - Simple cycle |  |  |  |  | 0.083649 | 0.083649 | 0.083649 | 0.083649
26 | Biogas - Simple cycle with inlet fogging |  |  |  |  | 0.55678 | 0.68925 | 0.55678 | 0.68925
27 | Biogas - Combined cycle with wet cooling and inlet fogging |  |  |  |  | 1.3437 | 1.4762 | 1.1544 | 1.2869
28 | Biogas - Combined cycle with wet cooling |  |  |  |  | 0.87055 | 0.87055 | 0.6813 | 0.6813
29 | Biogas - Combined cycle with dry cooling and inlet fogging |  |  |  |  | 0.62453 | 0.757 | 0.47313 | 0.6056
30 | Biogas - Combined cycle with dry cooling |  |  |  |  | 0.1514 | 0.1514 | 0 | 0
31 | Biogas - Combined cycle, once-thru cooling |  |  |  |  | 9.084 | 75.7002 | 0.3785 | 0.3785
32 | Biogas - Steam turbine, once-thru cooling |  |  |  |  | 75.7002 | 189.2506 | 1.1355 | 1.1355
33 | Biogas - Steam turbine, wet cooling |  |  |  |  | 1.1355 | 3.028 | 0.9084 | 2.4224
| Biogas - Steam turbine, dry cooling |  |  |  |  | 0.1514 | 0.1514 | 0 | 0
34 | Biogas - Steam turbine, pond cooling |  |  |  |  | 1.1355 | 2.271 | 1.1355 | 1.8168
35
36

## Coal
Water Requirements for Coal Power Production
All Numbers in m3/MWh
| COAL | Withdrawal |  | Consumption
|  | m^3/MWh |  | m^3/MWh
| Item | Low | High | Low | High | Notes/Assumptions | Sources
| Surface Mining | 0.0051673 | 0.49236 | 0.005 | 0.052941 | Choose consumption higher value if revegetating 6150 kWh/ton of coal mined | [CH] (Gleick 1994) [CL] Set to Match WL [WL]Calculation based on (Gleick 1994) and NMA conversion [WH] Coal Text Book
| Underground Mining | 0.4462 | 0.4462 | 0.031764 | 0.21176 |  | [C](Gleick 1994) [WL]Calculation based on (Gleick 1994) and NMA conversion [WH] Coal Text Book
| Coal Washing | 0.012309 | 0.024618 | 0 | 0 | 80% of eastern and interior coal is washed | [W] (Gleick 1994) from (Chan et al. 2006)
| Pulverized Slurry Line | 0.030772 | 0.9 | 0.03 | 0.89999 |  | [CH](Gleick 1994) from (Chan et al. 2006) [WL]Coal Textbook [WH]Set to match CH [CL]Set to match WL
| Log Slurry Line | 0.0092317 | 0.27 | 0.009 | 0.27 | Saves up to 70% water of traditional slurry. | [W] & [C] (Liu 2002)
| IGCC (Gasification) | 0.18017 | 0.2376 | 0.094635 | 0.12757 | 500 MW plant | [W] & [C] (Klett 2005)
| IGCC Makeup Water (ex. Cooling) | 0.14839 | 0.38914 |  |  |  | [W] & [C] (Klett 2005)
| IGCC Process Losses |  |  | 0.094635 | 0.1287 |  | [W] & [C] (Klett 2005)
| IGCC Flue Gas Water Losses |  |  | 0.29148 | 0.40125 |  | [W] & [C] (Klett 2005)
| IGCC Wet Cooling | 2.2966 | 2.7921 | 2.2966 | 2.7921 |  | [W] & [C] (Klett 2005)
| IGCC Pond Cooling | 0.73808 | 1.4762 | 0.73808 | 1.1809 |  | [W] & [C] (Klett 2005)
| PC Combustion | 0.14345 | 0.16194 | 0 | 0 | 600MW pulverized coal plant. | [W] (Ziemkiewicz) [C]Hypothesis bc I can't find numbers
| PC Makeup Water (ex. Cooling) | 0.0071923 | 0.016656
| PC Process Losses |  |  | 0.030283 | 0.034069
| PC Flue Gas Water Losses |  |  | 0.35961 | 0.40504
| PC Flue Gas Desulfurization | 0.23536 | 0.405 | 0.23536 | 0.405
| PC Wet Cooling | 3.7089 | 4.1602 | 3.7089 | 3.7089 | Numbers are thermoelectic averages | [CH] (Feeley et al. 2005) [CL] (EPRI 2002) [WH] (Feeley et al. 2005) [WL] (EPRI 2002)
| PC Once-Through Cooling | 75.7002 | 189.2506 | 1.1355 | 1.1355 | 600MW pulverized coal plant. Uses 35% less water when paired with an IGCC plant | [W] (Ziemkiewicz) [C]Hypothesis bc I can't find numbers
| PC Pond Cooling | 1.1355 | 2.271 | 1.1355 | 1.8168 | Numbers from EPRI are thermoelectric averages | [C]&[W] (EPRI 2002)
| PC Hybrid Wet-Dry Cooling | 0.3785 | 3.6336 | 0.36336 | 3.3308 | Results in about 50% less water consumption than a conventional closed-loop wet cooling system Consumption is 20-80% of recirculating wet cooling Uses 35% less water when paired with an IGCC plant | [C] (EPRI 2002)
| PC Direct Dry Cooling | 0.094625 | 0.2271 | 0.09084 | 0.20818 | Dry cooling cuts consumption by 95% (Compared to wet cooling) Uses 35% less water when paired with an IGCC plant | (Queensland Govt DOE)
| PC Indirect Dry Cooling | 0.094625 | 0.2271 | 0.094058 | 0.20893 | Same as direct cooling Uses 35% less water when paired with an IGCC plant | N/A
| Coal Power Production Method | [6 empty] | Withdrawal Water Requirement (m3/MWh) |  | Consumptive Water Requirement (m3/MWh)
[8 empty] | Low | High | Low | High
Water Requirements Pre-Plant
| Surface Mining - Coal Washing - Pulverized Slurry | [6 empty] | 0.048249 | 1.417 | 0.035 | 0.95293
| Surface Mining - No Washing - Pulverized Slurry | [6 empty] | 0.03594 | 1.3924 | 0.035 | 0.95293
| Underground Mining - Coal Washing - Pulverized Slurry | [6 empty] | 0.48928 | 1.3708 | 0.061764 | 1.1118
| Underground Mining - No Washing - Pulverized Slurry | [6 empty] | 0.47697 | 1.3462 | 0.061764 | 1.1118
Water Requirements Plant
| Conventional Pulverized Combustion - Once-Through Cooling | [6 empty] | 76.0862 | 189.8342 | 1.7608 | 1.9796
| Conventional Pulverized Combustion - Direct Dry Cooling | [6 empty] | 0.48062 | 0.81069 | 0.7161 | 1.0523
| Conventional Pulverized Combustion - Indirect Dry Cooling | [6 empty] | 0.48062 | 0.81069 | 0.71931 | 1.053
| Conventional Pulverized Combustion - Hybrid Wet-Dry Cooling | [6 empty] | 0.48062 | 0.81069 | 0.71931 | 1.053
| Conventional Pulverized Combustion - Pond Cooling | [6 empty] | 80.9307 | 196.2653 | 6.6052 | 7.5054
| Conventional Pulverized Combustion - Wet Cooling | [6 empty] | 4.0949 | 4.7438 | 4.3342 | 4.5531
N/A | Gasification - Once-Through Cooling | [6 empty] | 49.5337 | 123.6396 | 1.2188 | 1.3956
N/A | Gasification - Direct Dry Cooling | [6 empty] | 0.39007 | 0.77435 | 0.53979 | 0.79284
N/A | Gasification - Indirect Dry Cooling | [6 empty] | 0.39007 | 0.77435 | 0.54188 | 0.79333
N/A | Gasification - Hybrid Wet-Dry Cooling | [6 empty] | 0.57459 | 2.9886 | 0.71693 | 2.8226
* | Gasification - Cooling Pond | [6 empty] | 1.0666 | 2.1029 | 1.2188 | 1.8384
* | Gasification - Wet Cooling | [6 empty] | 2.6252 | 3.4189 | 2.7774 | 3.4496
Total Water Requirements
1 | Surface Mining - Coal Washing - Pulverized Slurry - Conventional Pulverized Combustion - Once-Through Cooling | [6 empty] | 76.1345 | 191.2511 | 1.7958 | 2.9325
2 | Surface Mining - Coal Washing - Pulverized Slurry - Conventional Pulverized Combustion - Recirculating Cooling - Direct Dry Cooling | [6 empty] | 0.52887 | 2.2277 | 0.7511 | 2.0052
3 | Surface Mining - Coal Washing - Pulverized Slurry - Conventional Pulverized Combustion - Recirculating Cooling - Indirect Dry Cooling | [6 empty] | 0.52887 | 2.2277 | 0.75431 | 2.006
4 | Surface Mining - Coal Washing - Pulverized Slurry - Conventional Pulverized Combustion - Recirculating Cooling - Hybrid Wet-Dry Cooling | [6 empty] | 0.52887 | 2.2277 | 0.75431 | 2.006
5 | Surface Mining - Coal Washing - Pulverized Slurry - Conventional Pulverized Combustion - Recirculating Cooling - Pond Cooling | [6 empty] | 80.9789 | 197.6823 | 6.6402 | 8.4583
6 | Surface Mining - Coal Washing - Pulverized Slurry - Conventional Pulverized Combustion - Recirculating Cooling - Wet Cooling | [6 empty] | 4.1432 | 6.1607 | 4.3692 | 5.506
7 | Surface Mining - Coal Washing - Pulverized Slurry - Gasification - Once-Through Cooling | [6 empty] | 49.582 | 125.0566 | 1.2538 | 2.3485
8 | Surface Mining - Coal Washing - Pulverized Slurry - Gasification - Recirculating Cooling - Direct Dry Cooling | [6 empty] | 0.43832 | 2.1913 | 0.57479 | 1.7458
9 | Surface Mining - Coal Washing - Pulverized Slurry - Gasification - Recirculating Cooling - Indirect Dry Cooling | [6 empty] | 0.43832 | 2.1913 | 0.57688 | 1.7463
10 | Surface Mining - Coal Washing - Pulverized Slurry - Gasification - Recirculating Cooling - Hybrid Wet-Dry Cooling | [6 empty] | 0.62284 | 4.4056 | 0.75193 | 3.7755
11 | Surface Mining - Coal Washing - Pulverized Slurry - Gasification - Recirculating Cooling - Pond Cooling | [6 empty] | 1.1149 | 3.5199 | 1.2538 | 2.7914
12 | Surface Mining - Coal Washing - Pulverized Slurry - Gasification - Recirculating Cooling - Wet Cooling | [6 empty] | 2.6734 | 4.8358 | 2.8124 | 4.4026
13 | Surface Mining - No Washing - Pulverized Slurry - Conventional Pulverized Combustion - Once-Through Cooling | [6 empty] | 76.1222 | 191.2265 | 1.7958 | 2.9325
14 | Surface Mining - No Washing - Pulverized Slurry - Conventional Pulverized Combustion - Recirculating Cooling - Direct Dry Cooling | [6 empty] | 0.51656 | 2.203 | 0.7511 | 2.0052
15 | Surface Mining - No Washing - Pulverized Slurry - Conventional Pulverized Combustion - Recirculating Cooling - Indirect Dry Cooling | [6 empty] | 0.51656 | 2.203 | 0.75431 | 2.006
16 | Surface Mining - No Washing - Pulverized Slurry - Conventional Pulverized Combustion - Recirculating Cooling - Hybrid Wet-Dry Cooling | [6 empty] | 0.51656 | 2.203 | 0.75431 | 2.006
17 | Surface Mining - No Washing - Pulverized Slurry - Conventional Pulverized Combustion - Recirculating Cooling - Pond Cooling | [6 empty] | 80.9666 | 197.6577 | 6.6402 | 8.4583
18 | Surface Mining - No Washing - Pulverized Slurry - Conventional Pulverized Combustion - Recirculating Cooling - Wet Cooling | [6 empty] | 4.1309 | 6.1361 | 4.3692 | 5.506
19 | Surface Mining - No Washing - Pulverized Slurry - Gasification - Once-Through Cooling | [6 empty] | 49.5696 | 125.032 | 1.2538 | 2.3485
20 | Surface Mining - No Washing - Pulverized Slurry - Gasification - Recirculating Cooling - Direct Dry Cooling | [6 empty] | 0.42601 | 2.1667 | 0.57479 | 1.7458
21 | Surface Mining - No Washing - Pulverized Slurry - Gasification - Recirculating Cooling - Indirect Dry Cooling | [6 empty] | 0.42601 | 2.1667 | 0.57688 | 1.7463
22 | Surface Mining - No Washing - Pulverized Slurry - Gasification - Recirculating Cooling - Hybrid Wet-Dry Cooling | [6 empty] | 0.61053 | 4.3809 | 0.75193 | 3.7755
23 | Surface Mining - No Washing - Pulverized Slurry - Gasification - Recirculating Cooling - Pond Cooling | [6 empty] | 1.1026 | 3.4952 | 1.2538 | 2.7914
24 | Surface Mining - No Washing - Pulverized Slurry - Gasification - Recirculating Cooling - Wet Cooling | [6 empty] | 2.6611 | 4.8112 | 2.8124 | 4.4026
25 | Underground Mining - Coal Washing - Pulverized Slurry - Conventional Pulverized Combustion - Once-Through Cooling | [6 empty] | 76.5755 | 191.205 | 1.8225 | 3.0914
26 | Underground Mining - Coal Washing - Pulverized Slurry - Conventional Pulverized Combustion - Recirculating Cooling - Indirect Dry Cooling | [6 empty] | 0.96991 | 2.1815 | 0.77786 | 2.164
27 | Underground Mining - Coal Washing - Pulverized Slurry - Conventional Pulverized Combustion - Recirculating Cooling - Dry Cooling - Indirect | [6 empty] | 0.96991 | 2.1815 | 0.78108 | 2.1648
28 | Underground Mining - Coal Washing - Pulverized Slurry - Conventional Pulverized Combustion - Recirculating Cooling - Hybrid Wet-Dry Cooling | [6 empty] | 0.96991 | 2.1815 | 0.78108 | 2.1648
29 | Underground Mining - Coal Washing - Pulverized Slurry - Conventional Pulverized Combustion - Recirculating Cooling - Pond Cooling | [6 empty] | 81.42 | 197.6361 | 6.667 | 8.6171
30 | Underground Mining - Coal Washing - Pulverized Slurry - Conventional Pulverized Combustion - Recirculating Cooling - Wet Cooling | [6 empty] | 4.5842 | 6.1146 | 4.396 | 5.6648
31 | Underground Mining - Coal Washing - Pulverized Slurry - Gasification - Once-Through Cooling | [6 empty] | 50.023 | 125.0104 | 1.2806 | 2.5074
32 | Underground Mining - Coal Washing - Pulverized Slurry - Gasification - Recirculating Cooling - Direct Dry Cooling | [6 empty] | 0.87935 | 2.1452 | 0.60156 | 1.9046
33 | Underground Mining - Coal Washing - Pulverized Slurry - Gasification - Recirculating Cooling - Indirect Dry Cooling | [6 empty] | 0.87935 | 2.1452 | 0.60365 | 1.9051
34 | Underground Mining - Coal Washing - Pulverized Slurry - Gasification - Recirculating Cooling - Hybrid Wet-Dry Cooling | [6 empty] | 1.0639 | 4.3594 | 0.7787 | 3.9343
35 | Underground Mining - Coal Washing - Pulverized Slurry - Gasification - Recirculating Cooling - Pond Cooling | [6 empty] | 1.5559 | 3.4737 | 1.2806 | 2.9502
36 | Underground Mining - Coal Washing - Pulverized Slurry - Gasification - Recirculating Cooling - Wet Cooling | [6 empty] | 3.1145 | 4.7897 | 2.8391 | 4.5614
37 | Underground Mining - No Washing - Pulverized Slurry - Conventional Pulverized Combustion - Once-Through Cooling | [6 empty] | 76.5632 | 191.1804 | 1.8225 | 3.0914
38 | Underground Mining - No Washing - Pulverized Slurry - Conventional Pulverized Combustion - Recirculating Cooling - Indirect Dry Cooling | [6 empty] | 0.9576 | 2.1569 | 0.77786 | 2.164
39 | Underground Mining - No Washing - Pulverized Slurry - Conventional Pulverized Combustion - Recirculating Cooling - Dry Cooling - Indirect | [6 empty] | 0.9576 | 2.1569 | 0.78108 | 2.1648
40 | Underground Mining - No Washing - Pulverized Slurry - Conventional Pulverized Combustion - Recirculating Cooling - Hybrid Wet-Dry Cooling | [6 empty] | 0.9576 | 2.1569 | 0.78108 | 2.1648
41 | Underground Mining - No Washing - Pulverized Slurry - Conventional Pulverized Combustion - Recirculating Cooling - Pond Cooling | [6 empty] | 81.4076 | 197.6115 | 6.667 | 8.6171
42 | Underground Mining - No Washing - Pulverized Slurry - Conventional Pulverized Combustion - Recirculating Cooling - Wet Cooling | [6 empty] | 4.5719 | 6.09 | 4.396 | 5.6648
43 | Underground Mining - No Washing - Pulverized Slurry - Gasification - Once-Through Cooling | [6 empty] | 50.0107 | 124.9858 | 1.2806 | 2.5074
44 | Underground Mining - No Washing - Pulverized Slurry - Gasification - Recirculating Cooling - Direct Dry Cooling | [6 empty] | 0.86704 | 2.1206 | 0.60156 | 1.9046
45 | Underground Mining - No Washing - Pulverized Slurry - Gasification - Recirculating Cooling - Indirect Dry Cooling | [6 empty] | 0.86704 | 2.1206 | 0.60365 | 1.9051
46 | Underground Mining - No Washing - Pulverized Slurry - Gasification - Recirculating Cooling - Hybrid Wet-Dry Cooling | [6 empty] | 1.0516 | 4.3348 | 0.7787 | 3.9343
47 | Underground Mining - No Washing - Pulverized Slurry - Gasification - Recirculating Cooling - Pond Cooling | [6 empty] | 1.5436 | 3.4491 | 1.2806 | 2.9502
48 | Underground Mining - No Washing - Pulverized Slurry - Gasification - Recirculating Cooling - Wet Cooling | [6 empty] | 3.1021 | 4.7651 | 2.8391 | 4.5614

## Geothermal
Water Requirements for Geothermal Power Production
All Numbers in m3/MWh
GEOTHERMAL | Withdrawal |  | Consumption
| m^3/MWh |  | m^3/MWh
Item | Low | High | Low | High | Notes/Assumptions | Sources
Injection from external sources, water dominated system | 0 | 3.49 | 0 | 3.49 | High number reflects the only external injection program of its kind, in the Geysers | [W, C]Sass and Priest 2002, Dept of Oil, Gas, and Geothermal Resources 2005
Injection from external sources, steam dominated system | 0 | 3.49 | 0 | 3.49 | High number reflects the only external injection program of its kind, in the Geysers | [W, C]Sass and Priest 2002, Dept of Oil, Gas, and Geothermal Resources 2005
Cooling, once through | 0 | 54 | 0 | 0.246 | WL, CL from Bagnore, Italy; WH from Nesjavellir, Iceland. CH from Salton Sea Unit 6. The Iceland plant disposes of wastewater into groundwater flowing to a lake; maybe that explains the high. I believe it's like a once-through cooling system. Gleick says up to 15 m3/MWh if you need external water. The Geysers requires no external water for cooling (Gleick 1994). | [WH]Hagedoorn 2006, [CH] Adams et al. 2005 [WL]/[CL]Hagedoorn 2006
Cooling, wet recirculating (cooling towers) | 0 | 17.03 | 0 | 17.03 |  | [WL]/[CL]Adams et al. 2005, [WH]/[CH]Charles et al. 2006
Cooling, dry | 0 | 0 | 0 | 0 | Kagel mentions no numbers here; I am assuming the water required is negligible. If fossil plants withdraw such little water for dry cooling, I am assuming that small amount can be easily met with geothermal fluid (which we aren't counting). | [WH]/[CH]Kagel et al. 2005, USDOE 2006 [WL]/[CL]Kagel et al. 2005, USDOE 2006
FOR CALIFORNIA CASE STUDY, MORE SPECIFIC NUMBERS:
Cooling, Imperial Valley | 7.7 | 14.1 | 7.7 | 14.1
Cooling, other locations in California | 0 | 0.019 | 0 | 0.019
Geothermal Power Production Method
| Withdrawal Water Requirement (m3/MWh) |  | Consumptive Water Requirement (m3/MWh)
| Low | High | Low | High
Steam dominated, once through cooling | 0 | 57.49 | 0 | 3.736
Steam dominated, dry cooling | 0 | 3.49 | 0 | 3.49
Water dominated, once through cooling | 0 | 57.49 | 0 | 3.736
Water dominated, dry cooling | 0 | 3.49 | 0 | 3.49
Steam dominated, wet recirculating cooling | 0 | 20.52 | 0 | 20.52
Water dominated, wet recirculating cooling | 0 | 20.52 | 0 | 20.52
Special notes:
We are no longer considering geothermal fluid or steam in this spreadsheet.

## Hydro
Water Requirements for Hydroelectric Power Production
All Numbers in m3/MWh
| Hydroelectric | Withdrawal |  | Consumption
|  | m^3/MWh |  | m^3/MWh
| Item | Low | High | Low | High | Notes/Assumptions | Sources
| Evaporative Losses, <25 MW plant | 208.8 | 208.8 | 0.18 | 14.4 | Average water withdrawal statistics for that size facility. | Gleick 1992 [W,C/H,L]
| Evaporative Losses, >25 MW plant | 162 | 162 | 0.036 | 2.52 |  | Gleick 1992 [W,C/H,L]
Hydroelectric Power Production Method
[6 empty] | Withdrawal Water Requirement (m3/MWh) |  | Consumptive Water Requirement (m3/MWh)
[6 empty] | Low | High | Low | High
1 | Reservoir and Dam, < 25 MW capacity - Dam Height < Gross Static Head |  |  |  |  | 208.8 | 208.8 | 0.18 | 82.7
2 | Reservoir and Dam, < 25 MW capacity - Dam Height > Gross Static Head |  |  |  |  | 208.8 | 208.8 | 1.94 | 209
3 | Reservoir and Dam, > 25 MW capacity - Dam Height < Gross Static Head |  |  |  |  | 162 | 162 | 0.036 | 122
4 | Reservoir and Dam, > 25 MW capacity - Dam Height > Gross Static Head |  |  |  |  | 162 | 162 | 3.6 | 162
5 | "Run of River" Facility |  |  |  |  | 0 | 0 | 0 | 0 | Assumes that "run of river" facilities do not impound water, increasing rates of evaporation
6 | Facilities in aqueducts |  |  |  |  | 0 | 0 | 0 | 0 | Assumes that these facilities do not increase rates of evaporation above existing rates.
7

## Natural Gas
Water Requirements for Natural Gas Power Production
All Numbers in m3/MWh
NATURAL GAS | Withdrawal |  | Consumption
| m^3/MWh |  | m^3/MWh
Item | Low | High | Low | High | Assumptions | Source
Simple Cycle | 0.083649 | 0.083649 | 0.083649 | 0.083649 | Assumes a 500 MW plant | Maulbetsch 2006, EPRI, CATF et al. 2003
Combined cycle, wet cooling | 0.87055 | 0.87055 | 0.6813 | 0.6813
Combined cycle, dry cooling | 0.1514 | 0.1514 | 0 | 0
Combined cycle, once-thru cooling | 9.084 | 75.7002 | 0.3785 | 0.3785
Steam turbine, once-thru cooling | 75.7002 | 189.2506 | 1.1355 | 1.1355
Steam turbine, wet cooling | 1.1355 | 3.028 | 0.9084 | 2.4224
Steam turbine, dry cooling | 0.1514 | 0.1514 | 0 | 0
Steam turbine, pond cooling | 1.1355 | 2.271 | 1.1355 | 1.8168
Inlet fogging (additional option) | 0.47313 | 0.6056 | 0.47313 | 0.6056 |  | Maulbetsch 2006
Mining, combined cycle conversion technology | 0.036 | 0.036 | 0.036 | 0.036 | Assumes a conversion efficiency of 60% for combined cycle plants
Mining, Simple cycle conversion technology | 0.06 | 0.06 | 0.06 | 0.06 | Assumes a conversion efficiency of 36% (from thermal to electric Joules), source - Gleick (1994)
Transportation, combined cycle conversion technology | 0.018 | 0.018 | 0.018 | 0.018 | Assumes a conversion efficiency of 60% for combined cycle plants
Transportation, simple cycle conversion technology | 0.03 | 0.03 | 0.03 | 0.03 | Assumes a conversion efficiency of 36% (from thermal to electric Joules), source - Gleick (1994)
Other (hotel load) | 0 | 0.36 | 0 | 0.36 | Gleick says 0.36, but I use 0 in other places to avoid mismatching sources.
Natural Gas Power Production Method
| Withdrawal Water Requirement (m3/MWh) |  | Consumptive Water Requirement (m3/MWh)
| Low | High | Low | High
Simple cycle, no inlet fogging | 0.11605 | 0.11605 | 0.11605 | 0.11605
Simple cycle, inlet fogging | 0.58918 | 0.72165 | 0.58918 | 0.72165
Combined cycle, wet cooling, inlet fogging | 1.3761 | 1.5086 | 1.1868 | 1.3193
Combined cycle, wet cooling, no inlet fogging | 0.90295 | 0.90295 | 0.7137 | 0.7137
Combined cycle, dry cooling, inlet fogging | 0.65693 | 0.7894 | 0.50553 | 0.638
Combined cycle, dry cooling, no inlet fogging | 0.1838 | 0.1838 | 0.0324 | 0.0324
Combined cycle, once-thru cooling | 9.1164 | 75.7326 | 0.4109 | 0.4109
Steam turbine, once-thru cooling | 76.0926 | 189.643 | 1.5279 | 1.5279
Steam turbine, wet cooling | 1.5279 | 3.4204 | 1.3008 | 2.8148
Steam turbine, dry cooling | 0.5438 | 0.5438 | 0.3924 | 0.3924
Steam turbine, pond cooling | 1.5279 | 2.6634 | 1.5279 | 2.2092
Note on A7: %USERNAME%: Maultbesch (2006), assumes 500 MW plant

## Nuclear
Water Requirements for Nuclear Power Production
All Numbers in m3/MWh
NUCLEAR |  | Withdrawal |  | Consumption
|  | m^3/MWh |  | m^3/MWh
Item |  | Low | High | Low | High | Notes/Assumptions | Sources
Surface Uranium Mining |  | 0.23226 | 0.23226 | 0 | 0 | only for surface mining | [W] & [C]: Gleick 1993
Underground Uranium Mining |  | 0.0023227 | 0.0023227 | 0 | 0 | only for underground mining | [W] & [C]: Gleick 1993
Processing |  | 0.7548 | 0.9058 | 0.4522 | 0.5365 | processing includes: milling, conversion, enrichment, fuel fabrication, fuel reprocessing | [W] & [C]: Gleick 1993
BWR | once-thru cooling | 94.6253 | 227.1007 | 0.3785 | 5.035 | for BWR assuming once-through cooling | [W]: EPRI 2002; [C/L]: Hoffman et al. 2004; [C/H] Pace University Environmental Law Center 1990;
| natural draft wet cooling tower | 3.028 | 5.6775 | 1.514 | 5.6775 |  | [W/L]:EPRI 2002; [W/H]:Hoffman et al. 2004; [C/H]:EPRI 2002; [C/L]: Hoffman et al. 2004
| closed cycle cooling pond, lake, or reservoir | 2.7252 | 4.1635 | 2.7252 | 2.7252 |  | [W] & [C]: EPRI 2002
PWR | once-thru cooling | 94.6253 | 227.1007 | 0.3785 | 1.514 |  | [W] EPRI 2002; [C/L]: Hoffman et al. 2004; [C/H]: EPRI 2002
| natural draft wet cooling tower | 3.028 | 5.6775 | 1.514 | 5.6775 |  | [W/L]:EPRI 2002; [W/H]:Hoffman et al. 2004; [C/H]:EPRI 2002; [C/L]: Hoffman et al. 2004
| closed cycle cooling pond, lake, or reservoir | 2.7252 | 4.1635 | 2.7252 | 3.233 |  | [W] EPRI 2002; [C/L]: EPRI 2002; [C/H]: Pace University Environmental Law Center 1990
Nuclear Power Production Method
|  | Withdrawal Water Requirement (m3/MWh) |  | Consumptive Water Requirement (m3/MWh)
|  | Low | High | Low | High
1 | BWR - Surface Mining - Once-through | 95.6123 | 228.2387 | 0.8307 | 5.5715
2 | BWR - Underground Mining - Once-through | 95.3824 | 228.0088 | 0.8307 | 5.5715
3 | BWR - Surface Mining - Closed-cycle - Natural Draft Wet Cooling Tower | 4.0151 | 6.8156 | 1.9662 | 6.214
4 | BWR - Underground Mining - Closed-cycle - Natural Draft Wet Cooling Tower | 3.7851 | 6.5856 | 1.9662 | 6.214
5 | BWR - Surface Mining - Closed-cycle - Cooling pond, lake, or reservoir | 3.7123 | 5.3016 | 3.1774 | 3.2617
6 | BWR - Underground Mining - Closed-cycle - Cooling pond, lake, or reservoir | 3.4823 | 5.0716 | 3.1774 | 3.2617
7 | PWR - Surface Mining - Once-through | 95.6123 | 228.2387 | 0.8307 | 2.0505
8 | PWR - Underground Mining - Once-through | 95.3824 | 228.0088 | 0.8307 | 2.0505
9 | PWR - Surface Mining - Closed Cycle - Natural Draft Wet Cooling Tower | 4.0151 | 6.8156 | 1.9662 | 6.214
10 | PWR - Underground Mining - Closed Cycle - Natural Draft Wet Cooling Tower | 3.7851 | 6.5856 | 1.9662 | 6.214
11 | PWR - Surface Mining - Closed Cycle - Cooling pond, lake, or reservoir | 3.7123 | 5.3016 | 3.1774 | 3.7695
12 | PWR - Underground Mining - Closed Cycle - Cooling pond, lake, or reservoir | 3.4823 | 5.0716 | 3.1774 | 3.7695
Pace University Environmental Law Center 1990
Hoffman et al. 2004: http://www.netl.doe.gov/technologies/coalpower/ewr/pubs/Estimating%20Freshwater%20Needs%20to%202025.pdf
EPRI 2002: Water & Sustainability (Volume 3): U.S. Water Consumption for Power Production - The Next Half Century

## Oil
Water Requirements for Oil Power Production
All Numbers in m3/MWh
OIL | Withdrawal |  | Consumption
| m^3/MWh |  | m^3/MWh
Item | Low | High | Low | High | Notes/Assumptions | Sources
Oil Shale Mining - Direct Aboveground Retorting (AGR) | 0.02796 | 0.045447 | 0.02796 | 0.045447 | All calculations assume one barrel of crude oil (42 gallons) has an energy capacity of 1700 kWh. Assumes a 50,000 bbl/day facility. The cited reference describes all water used as "consumed water" and does not distinguish from "withdrawn water". The quality of the water may, indeed, mean that it is effectively consumed; however, there may be some opportunity for reclaiming water. We do not tackle that question. "Other" uses include water for disposal and revegetation, dust control during extraction, plant utilities, and on-site power needs. | Emerging Issues for Fossil Energy and Water, 2006 [W,C/H,L]
Oil Shale Mining - Indirect AGR | 0.035348 | 0.046756 | 0.035348 | 0.046756
Oil Shale Mining - Modified In-situ (MIS)/AGR | 0.013466 | 0.014027 | 0.013466 | 0.014027
Oil Shale Mining - Modified In-situ (MIS) | 0.019638 | 0.019638 | 0.019638 | 0.019638
Oil Shale Processing - Direct Aboveground Retorting (AGR) | 0.088182 | 0.11109 | 0.088182 | 0.11109
Oil Shale Processing - Indirect AGR | 0.13746 | 0.20105 | 0.13746 | 0.20105
Oil Shale Processing - Modified In-situ (MIS)/AGR | 0.12119 | 0.14494 | 0.12119 | 0.14494
Oil Shale Processing - Modified In-situ (MIS) | 0.10015 | 0.10015 | 0.10015 | 0.10015
Oil Shale (Other) - Direct Aboveground Retorting (AGR) | 0.077428 | 0.12119 | 0.077428 | 0.12119
Oil Shale (Other) - Indirect AGR | 0.18067 | 0.27586 | 0.18067 | 0.27586
Oil Shale (Other) - Modified In-situ (MIS)/AGR | 0.071817 | 0.093512 | 0.071817 | 0.093512
Oil Shale (Other) - Modified In-situ (MIS) | 0.076586 | 0.076586 | 0.076586 | 0.076586
Combined cycle, once-thru cooling | 9.084 | 75.7002 | 0.3785 | 0.3785 | Analysis assumes that oil cooling is the same as natural gas cooling. | EPRI, CATF et al. 2003
Combined cycle, wet cooling | 0.87055 | 0.87055 | 0.6813 | 0.6813
Combined cycle, dry cooling | 0.1514 | 0.1514 | 0 | 0
Steam turbine, once-thru cooling | 75.7002 | 189.2506 | 1.1355 | 1.1355
Steam turbine, wet cooling | 1.1355 | 3.028 | 0.9084 | 2.4224
Steam turbine, dry cooling | 0.1514 | 0.1514 | 0 | 0
Steam turbine, pond cooling | 1.1355 | 2.271 | 1.1355 | 1.8168
Drilling | 0.010836 | 32.04 | 0.010836 | 32.04 |  | Gleick 1994
Refining | 0.09 | 0.432 | 0.09 | 0.432 |  | Gleick 1994
Other (hotel load) | 0.252 | 0.252 | 0.252 | 0.252 |  | Gleick 1994
Oil Power Production Method
| Withdrawal Water Requirement (m3/MWh) |  | Consumptive Water Requirement (m3/MWh) |  | average
| Low | High | Low | High
Combined cycle, once-thru cooling | 9.4369 | 108.4242 | 0.73134 | 33.1025 | 58.9305
Combined cycle, wet cooling | 1.2234 | 33.5946 | 1.0341 | 33.4053 | 17.409
Combined cycle, dry cooling | 0.50424 | 32.8754 | 0.35284 | 32.724 | 16.6898
Steam turbine, once-thru cooling | 76.0531 | 221.9746 | 1.4883 | 33.8595 | 149.0138
Steam turbine, wet cooling | 1.4883 | 35.752 | 1.2612 | 35.1464 | 18.6202
Steam turbine, dry cooling | 0.50424 | 32.8754 | 0.35284 | 32.724 | 16.6898
Steam turbine, pond cooling | 1.4883 | 34.995 | 1.4883 | 34.5408 | 18.2417
Oil Shale - Direct Aboveground Retorting - Combined cycle, once-thru cooling | 9.2776 | 75.978 | 0.57207 | 0.65623 | 42.6278
Oil Shale - Direct Aboveground Retorting - Combined cycle, wet cooling | 1.0641 | 1.1483 | 0.87487 | 0.95903 | 1.1062
Oil Shale - Direct Aboveground Retorting - Combined cycle - Dry cooling | 0.34497 | 0.42913 | 0.19357 | 0.27773 | 0.38705
Oil Shale - Direct Aboveground Retorting - Steam turbine - Once-through cooling | 75.8938 | 189.5283 | 1.3291 | 1.4132 | 132.711
Oil Shale - Direct Aboveground Retorting - Steam turbine - wet cooling | 1.3291 | 3.3057 | 1.102 | 2.7001 | 2.3174
Oil Shale - Direct Aboveground Retorting - Steam turbine - pond cooling | 1.3291 | 2.5487 | 1.3291 | 2.0945 | 1.9389
Oil Shale - Indirect Aboveground Retorting - Combined cycle, once-thru cooling | 9.4375 | 76.2239 | 0.73198 | 0.90217 | 42.8307
Oil Shale - Indirect Aboveground Retorting - Combined cycle, wet cooling | 1.224 | 1.3942 | 1.0348 | 1.205 | 1.3091
Oil Shale - Indirect Aboveground Retorting - Combined cycle - Dry cooling | 0.50488 | 0.67507 | 0.35348 | 0.52367 | 0.58997
Oil Shale - Indirect Aboveground Retorting - Steam turbine - Once-through cooling | 76.0537 | 189.7742 | 1.489 | 1.6592 | 132.914
Oil Shale - Indirect Aboveground Retorting - Steam turbine - wet cooling | 1.489 | 3.5517 | 1.2619 | 2.9461 | 2.5203
Oil Shale - Indirect Aboveground Retorting - Steam turbine - pond cooling | 1.489 | 2.7947 | 1.489 | 2.3405 | 2.1418
Oil Shale - Modified In-Situ/AGR - Combined cycle, once-thru cooling | 9.2905 | 75.9527 | 0.58498 | 0.63098 | 42.6216
Oil Shale - Modified In-Situ/AGR - Combined cycle, wet cooling | 1.077 | 1.123 | 0.88778 | 0.93378 | 1.1
Oil Shale - Modified In-Situ/AGR - Combined cycle - Dry cooling | 0.35788 | 0.40388 | 0.20647 | 0.25248 | 0.38088
Oil Shale - Modified In-Situ/AGR - Steam turbine - Once-through cooling | 75.9067 | 189.5031 | 1.342 | 1.388 | 132.7049
Oil Shale - Modified In-Situ/AGR - Steam turbine - wet cooling | 1.342 | 3.2805 | 1.1149 | 2.6749 | 2.3112
Oil Shale - Modified In-Situ/AGR - Steam turbine - pond cooling | 1.342 | 2.5235 | 1.342 | 2.0693 | 1.9327
Oil Shale - Modified In-Situ - Combined cycle, once-thru cooling | 9.2804 | 75.8966 | 0.57488 | 0.57488 | 42.5885
Oil Shale - Modified In-Situ - Combined cycle, wet cooling | 1.0669 | 1.0669 | 0.87768 | 0.87768 | 1.0669
Oil Shale - Modified In-Situ - Combined cycle - Dry cooling | 0.34778 | 0.34778 | 0.19638 | 0.19638 | 0.34778
Oil Shale - Modified In-Situ - Steam turbine - Once-through cooling | 75.8966 | 189.4469 | 1.3319 | 1.3319 | 132.6718
Oil Shale - Modified In-Situ - Steam turbine - wet cooling | 1.3319 | 3.2244 | 1.1048 | 2.6188 | 2.2781
Oil Shale - Modified In-Situ - Steam turbine - pond cooling | 1.3319 | 2.4674 | 1.3319 | 2.0132 | 1.8996

## Solar
Water Requirements for Solar Power Production
All Numbers in m3/MWh
SOLAR | Withdrawal |  | Consumption
| m^3/MWh |  | m^3/MWh
Item | Low | High | Low | High | Notes/Assumptions | Sources
Parabolic Trough Plant - wet cooling | 2.8 | 2.87 | 2.8 | 2.87 | Withdrawn is equivilant to consumed when withdrawn numbers are not available. | Stoddard, et al.2006 [W,C/L]; The Last Straw [W,C/H]
Parabolic Dish-Engine - dry cooling | 0 | 0 | 0 | 0 | No cooling required. | Stoddard, et al.2006 [W,C/H,L]
Power Tower - wet cooling | 2.4 | 2.8 | 2.4 | 2.8 |  | Solar Paces 2007 [W,C/L]; Stoddard et al. 2006 [W,C/H]
PV - Distributed (Rooftop) Systems | 0 | 0 | 0 | 0 | No cooling required. | The Last Straw; Stoddard et al. [W,C/H,L]
PV - Large Centralized Plants | 0 | 0 | 0 | 0 | No cooling required.
PV - Concentrating PV Systems | 0 | 0 | 0 | 0 | No cooling required.
Parabolic Trough Plant washing | 0.14 | 0.27 | 0.14 | 0.27 | High number found by subtracting the cooling water amt from the cooling and process water amt listed for this technology in the Last Straw | Stoddard, et al.2006 [W,C/L], Direct Communication, Mike Roverson, Kramer Junction [W,C/L], Last Straw [W,C/H]
Parabolic Dish-Engine washing | 0 | 0 | 0 | 0 |  | Stoddard, et al.2006 [W,C/H,L]
Power Tower washing | 0 | 0.14 | 0 | 0.14 | Assumed to be roughly equal to washing needs of a Parabolic Trough plant as both have large mirror fields.
PV - Distributed (Rooftop) Systems washing | 0.00379 | 0.114 | 0.00379 | 0.114 | Number for PV washing requirments used for both large plants and distributed gen (rooftop). | The Last Straw; AWEA Website 2006
PV - Large Centralized Plant washing | 0 | 0.114 | 0 | 0.114 | Number for PV washing requirments used for both large plants and distributed gen (rooftop). | AWEA Website 2006
PV - Concentrating PV Systems washing | 0 | 0 | 0 | 0 |  | Stoddard, et al.2006
Solar Power Production Method
| Withdrawal Water Requirement (m3/MWh) |  | Consumptive Water Requirement (m3/MWh)
| Low | High | Low | High
CSP - Parabolic Trough System | 2.94 | 3.14 | 2.94 | 3.14
CSP - Parabolic Dish-Engine System | 0 | 0 | 0 | 0
CSP - Power Tower Plant | 2.54 | 2.8 | 2.54 | 2.8
PV - Distributed (Rooftop) Systems | 0.00379 | 0.114 | 0.00379 | 0.114
PV - Large Centralized Plant | 0 | 0.114 | 0 | 0.114
PV - Concentrating PV Systems | 0 | 0 | 0 | 0

## Wind
Water Requirements for Wind Power Production
All Numbers in m3/MWh
| WIND | Withdrawal |  | Consumption
|  | m^3/MWh |  | m^3/MWh
| Item | Low | High | Low | High | Notes/Assumptions | Sources
| Cleaning medium sized wind farms | 0 | 0.00379 | 0 | 0.00379 | If the wind turbines are never cleaned, then the withdrawal and consumption equals zero | [W/L]: van Dam; [W/H]: AWEA 2006; [C/L]: van Dam; [C/H]: AWEA 2006
| Cleaning large sized wind farms | 0 | 0.00247 | 0 | 0.00247 | If the wind turbines are never cleaned, then the withdrawal and consumption equals zero Wind farms can operate at 30% of nameplate capacity If washed, turbines are washed 3 times/year Each turbine uses 40 gallons per washing | [W/L]: van Dam; [W/H]: J. Harris 2006; [C/L]: van Dam; [C/H]: J. Harris 2006
Wind Power Production Method
|  | Withdrawal Water Requirement (m3/MWh) |  | Consumptive Water Requirement (m3/MWh)
|  | Low | High | Low | High
1 | Medium sized wind farm | 0 | 0.00379 | 0 | 0.00379
2 | Large sized wind farm | 0 | 0.00247 | 0 | 0.00247

## ConversionFactors
Conversion of Units
Instructions: insert the value you have in the left box, and the coversion will be done automatically to right box
Volume/energy unit | [5 empty] | Quick reference/conversion
130 | gal/kWh | = | 492.0515 | m^3/MWh |  | 1 | MW | = | 1000 | kW
Energy
65 | gal/MWh | = | 0.24603 | m^3/MWh |  | 1 | kWh | = | 3600000 | Joules
[6 empty] | 1000000000000 | J | = | 277777.7778 | kWh
54 | liters/kWh | = | 54 | m^3/MWh |  | 1 | GJ | = | 277.8 | kWh
[6 empty] | 1e+18 | J | = | 278000000000 | kWh
1.1613 | ft^3/MWs | = | 118.3983 | m^3/MWh |  | 1 barrel crude oil |  | = | 5800000 | Btu
[6 empty] | 1 barrel crude oil |  | = | 1700 | kWh
1302083.3333 | gal/MWd | = | 205.35 | m^3/MWh |  | 1 | J | = | 2.78e-07 | kWh
Volume
195 | Mg/GJ | = | 701.9438 | m^3/MWh |  | 1 | m^3 | = | 1000 | liters
[6 empty] | 1 | m^3 | = | 264.2 | gallons (U.S.)
2.62e-06 | ac-ft/kWh | = | 3.2331 | m^3/MWh |  | 1 | m^3 | = | 35.31 | ft^3
[6 empty] | 1234 | m^3 | = | 1 | acre-foot
2.5e-11 | m^3/J |  | 0.09 | m^3/MWh |  | 1 | km^3 | = | 1000000000 | m^3
[6 empty] | 1 | Mg (Million grams) | = | 1 | m^3
70 | acre-ft/MWe | = | 86.38 | m^3/kW |  | 1 | megagallon | = | 378.5412 | m^3
45 | km^3/10^18 J | = | 161.8705 | m^3/MWh
64.516 | m^3/10^12 J | = | 0.23226 | m^3/MWh
4.32e-06 | m^3/kWh | = | 1.201e-12 | m^3/J
2000 | kWh/megagallon | = | 0.52834 | kWh/m^3
652 | kWh/af |  | 0.52858 | kWh/m^3
Note on L13: stellinghuisen reference: http://www.eia.doe.gov/kids/energyfacts/science/energy_calculator.html#oilcalc
Note on L14: stellinghuisen: reference: http://www.eia.doe.gov/kids/energyfacts/science/energy_calculator.html#oilcalc